MPL SIMULATION LIBRARY

Development Roadmap & Technical Specification

Mechanical Pumped Loop — Two-Phase Thermal Management

Electronics Cooling / Data Centers

| Application | Electronics cooling / Data centers |
| --- | --- |
| Topology | Single loop with accumulator |
| Power range | Up to 1 kW |
| Working fluids | Acetone · R1233zde · R1234yf (condenser: water) |
| Flow model | 1D Homogeneous Equilibrium Model (HEM) |
| Language | Python 3.10+ · CoolProp · NumPy · SciPy |
| Scope | Steady-state → Dynamic (Moving Boundary) → Stability analysis |

Version 1.0 — April 2026

# 1. Project Overview

This document defines the complete development roadmap for an open-source Python library to simulate Mechanical Pumped Loops (MPL) used in two-phase thermal management of power electronics and data center infrastructure.

The library is designed following a component-based, equation-oriented architecture that allows both steady-state (SS) and dynamic simulation, validation against published experimental data, and parametric analysis of system stability.

## 1.1 Objectives

- Build a modular, component-based Python library for MPL simulation

- Implement steady-state models for all loop components (pump, evaporator, condenser, accumulator, pipes)

- Validate against published experimental datasets from literature

- Extend to dynamic simulation using the Moving Boundary Method (MBM)

- Analyze system stability: Ledinegg instability, Density Wave Oscillations (DWO), Pressure Drop Oscillations (PDO)

- Support multiple working fluids and interchangeable correlation sets

- Enable testing of different loop architectures and component orderings

## 1.2 Physical basis

The library is grounded in the Homogeneous Equilibrium Model (HEM) as formulated by Dogan (1983) and applied by Kokate & Park (2023) for P2PL systems. The governing 1D conservation equations for two-phase flow are:

- Continuity:  ∂ρ/∂t + ∂G/∂z = 0

- Momentum:   ∂G/∂t + ∂(G²/ρ)/∂z = −∂P/∂z − ρg − 2f G²/ρd

- Energy:      ∂(ρe)/∂t + ∂(Gh)/∂z = (4/d) α(T_w − T_l)

Mixture properties follow HEM assumptions: equal phase velocities, thermodynamic equilibrium at saturation. The state is fully defined by pressure P and specific enthalpy h (per VanGerner 2016).

# 2. Literature Classification

The 25 papers in the project knowledge base have been classified by their utility for the simulation library. Priority ratings reflect relevance to implementation.

## Category A — System Overview & Architecture

| Reference | Key contribution | Priority | Use |
| --- | --- | --- | --- |
| Zhang 2019 / Zhan 2019 | Review MPCL: operating principle, fluids, applications | ★★★ | System scope |
| Middelhuis 2024 | Review MPL experiments, modular model + validation (CO2) | ★★★ | Architecture |
| Jie 2008 | Experimental dual-evaporator MPCL with CO2 | ★★ | Validation |
| Sunada 2016 | 2-phase MPFL architecture for spacecraft, 1D model | ★★ | Architecture |

## Category B — Steady-State Models

| Reference | Key contribution | Priority | Use |
| --- | --- | --- | --- |
| Kokate & Park 2023 + PhD 2024 | SS P2PL model, microchannel evaporator, Shah HTC, HEM | ★★★ | SS template |
| Wang 2023 | MPL modeling for data centers, full cycle SS | ★★★ | SS cycle |
| Li 2021 + Li 2022 | Experimental + control MPL with acetone — primary validation | ★★★ | Validation |

## Category C — Dynamic Models

| Reference | Key contribution | Priority | Use |
| --- | --- | --- | --- |
| Cho 2025 | Dynamic MPL model, Moving Boundary Method | ★★★ | MBM template |
| VanGerner 2016 | 1D dynamic model, MacCormack scheme, CO2, (H,P) state vars | ★★★ | Numerics |
| Truster 2024 | MPC control + pressure-controlled accumulator, R134a | ★★★ | Control |
| Leveque 2024 | MPL dynamics, transient behavior analysis | ★★ | Validation |
| Terpstra 2015 | Full loop dynamic model | ★★ | Reference |

## Category D — HTC & Pressure Drop Correlations

| Reference | Key contribution | Priority | Use |
| --- | --- | --- | --- |
| Kim & Mudawar 2012 | Universal HTC correlation, mini/micro-channels, multi-fluid | ★★★ | HTC alt. |
| Kim & Mudawar 2013 | Flow boiling ΔP in mini/micro-channels, 2378 data points | ★★★ | Primary ΔP |
| Gholamreza 2016 I+II | HTC + ΔP in metal-foam tubes, homogeneous model validation | ★★ | Reference |

## Category E — Accumulator & Instabilities

| Reference | Key contribution | Priority | Use |
| --- | --- | --- | --- |
| Lee 2022 | Accumulator position vs. PDO/PCI stability, experimental | ★★★ | Stability |
| Dogan 1983 | HEM 1D transient, DWO, Ledinegg — foundational equations | ★★★ | Foundation |
| Duda 2023 | HTC data centers, two-phase context | ★★ | Context |

## Category F — Fluid Selection & Other

| Reference | Key contribution | Priority | Use |
| --- | --- | --- | --- |
| Gerner 2014 | Figure of Merit for working fluid selection in MPL | ★★★ | Fluid FOM |
| Garimella 2017 | Semi-empirical model, jet impingement HTC | ★ | Reference |
| Furst 2017 | MPL architecture comparison | ★★ | Architecture |

# 3. Technology Stack & Repository Structure

## 3.1 Python dependencies

| Package | Purpose | Notes |
| --- | --- | --- |
| CoolProp 7.2+ | Thermodynamic + transport properties | Primary EOS backend |
| NumPy | Array math, linear algebra | Core numerics |
| SciPy | ODE solvers (BDF/Radau), Newton-Raphson, fsolve | SS + dynamic solvers |
| Pandas | Experimental data I/O, results management | Validation workflow |
| Matplotlib | Plotting, phase diagrams, stability maps | Visualization |
| pytest | Unit + integration testing per module | CI testing |
| Pydantic (optional) | Parameter validation for component inputs | Phase 3+ |

## 3.2 Repository structure

mpl_sim/

├── mpl/                          # Core library

│   ├── fluid_properties.py       # FluidState (CoolProp wrapper) ← DONE

│   ├── correlations.py           # HTC + ΔP correlations (Shah, Kim 2013)

│   ├── components/

│   │   ├── base.py               # Component abstract class + port definition

│   │   ├── pipe.py               # Single-phase + two-phase pipe

│   │   ├── evaporator.py         # Microchannel evaporator SS

│   │   ├── condenser.py          # Plate HX condenser SS

│   │   ├── pump.py               # Pump curve model

│   │   └── accumulator.py        # Gas-charged / bladder accumulator

│   ├── loop.py                   # Loop assembler + Newton-Raphson SS solver

│   ├── dynamic/

│   │   ├── mbm.py                # Moving Boundary Model equations

│   │   └── solver.py             # BDF/Radau ODE integrator wrapper

│   └── stability.py              # Ledinegg criterion, eigenvalue analysis

├── tests/

│   ├── test_fluid_properties.py  # ← DONE (67 tests passing)

│   ├── test_correlations.py

│   ├── test_components/

│   └── test_loop.py

├── validation/                   # Experimental comparison scripts

│   ├── kokate2023/

│   ├── li2021_acetone/

│   └── wang2023/

├── examples/

│   ├── 01_fluid_state_demo.py

│   ├── 02_single_evaporator_SS.py

│   └── 03_full_loop_SS.py

└── docs/                         # This roadmap + module specs

# 4. Development Phases

| Phase | Description | Output files | Status |
| --- | --- | --- | --- |
| 0 | Scope definition: topology, fluids, model fidelity, stack | This document | Completado |
| 1 | Fluid properties module — CoolProp wrapper, HEM properties | fluid_properties.py | Completado |
| 2 | Correlation library — HTC (Shah) + ΔP (Kim 2013, homogeneous) | correlations.py | Completado |
| 3 | Component base class + pipe SS model | base.py, pipe.py | Completado |
| 4 | Evaporator SS model (microchannel, zones) | evaporator.py | Completado |
| 5 | Condenser SS model (plate HX, water-refrigerant) | condenser.py | Completado |
| 6 | Pump model (characteristic curve) + accumulator SS | pump.py, accumulator.py | Completado |
| 7 | Loop assembler + Newton-Raphson SS solver | loop.py | Completado |
| 8 | Steady-state validation vs. Kokate 2023, Li 2021 (acetone), Wang 2023 | validation/ | Pendiente |
| 9 | Moving Boundary Model — dynamic evaporator + condenser equations | mbm.py | Pendiente |
| 10 | Dynamic accumulator model + loop ODE assembly + BDF solver | solver.py | Pendiente |
| 11 | Dynamic validation vs. Truster 2024, VanGerner 2016, Leveque 2024 | validation/dynamic/ | Pendiente |
| 12 | Stability analysis — Ledinegg, DWO eigenvalues, PDO simulation | stability.py | Pendiente |

# 5. Module Specifications

## 5.1 fluid_properties.py  ✓ COMPLETE

Status: implemented and tested (67/67 tests passing). Provides FluidState — the central state object passed between all components.

| Item | Detail |
| --- | --- |
| Primary inputs | fluid (str), P [Pa], h [J/kg] |
| State outputs | T, ρ, x, α, h_fg, μ, μ_tp, k, Pr, σ, T_sat, h_l, h_v, ρ_l, ρ_v, P_red |
| Phase detection | Liquid / Two-phase / Vapor — automatic from (P, h) |
| HEM density | 1/ρ = x/ρ_v + (1−x)/ρ_l (Dogan 1983, Eq. 4) |
| Void fraction | α = 1/(1 + (1−x)/x · ρ_v/ρ_l) (homogeneous) |
| μ_tp | Cicchitti: μ_tp = x·μ_v + (1−x)·μ_l (Kim 2013, Table 1) |
| Fallbacks | Acetone μ: Letsou-Stiel (~10%); k: Latini (~15%). Warned at runtime. |
| Constructors | from_Ph · from_PT · from_Px · from_Tsat |
| Fluids tested | Acetone · R1233ZDE · R1234YF · R134a · Water · CO2 |

## 5.2 correlations.py  — Next to implement

Pluggable correlation library using a Strategy Pattern. Each correlation is a callable that accepts a FluidState and geometry parameters and returns α_HTC [W/m²·K] or ΔP [Pa/m].

### HTC correlations (flow boiling):

| Correlation | Formula summary | Priority | Reference |
| --- | --- | --- | --- |
| Shah (1982) | α = max(α_cb, α_nb); α_cb = α_l·(1.8/N^0.8); MAE 37.2% vs Kokate | ★★★ | Kokate 2023 |
| Kim & Mudawar 2012 | Universal mini/micro-channel, We, Ca, Re based | ★★★ | Kim 2012 |
| Kandlikar-Balasubramanian | Minichannel, nucleate-to-convective transition | ★★ | Kokate 2023 |
| Dittus-Boelter | Single-phase: Nu = 0.023·Re^0.8·Pr^0.4 | ★★★ | Kokate 2023 |

### Pressure drop correlations:

| Correlation | Notes | Reference |
| --- | --- | --- |
| Homogeneous (Cicchitti μ_tp) | dP/dz = 2f_tp G²/(D·ρ_tp); Blasius f_tp. Best for low-x flows | Kim 2013, Dogan 1983 |
| Kim & Mudawar 2013 | Lockhart-Martinelli type, 2378 boiling data points, mini/micro | Kim 2013 |
| Muller-Steinhagen & Heck | Simple, used by Kokate 2023: ΔP = [A + 2(B−A)x]·(1−x)^(1/3) + Bx³ | Kokate 2023 |

Interface design (Strategy Pattern):

class HTCCorrelation(Protocol):

def __call__(self, state: FluidState, G: float, D_h: float,

q_flux: float, **kwargs) -> float: ...  # [W/m²·K]

class DPCorrelation(Protocol):

def __call__(self, state: FluidState, G: float, D_h: float,

L: float, **kwargs) -> float: ...  # [Pa]

## 5.3 components/base.py

Abstract base class that all components inherit. Defines the port interface for connecting components into a loop.

@dataclass

class Port:

state: FluidState   # thermodynamic state

mdot:  float        # mass flow rate [kg/s]

class Component(ABC):

inlet:  Port        # upstream connection

outlet: Port        # downstream connection

@abstractmethod

def solve_ss(self) -> Port: ...  # steady-state solution

@abstractmethod

def pressure_drop(self) -> float: ...  # [Pa]

@abstractmethod

def heat_transfer(self) -> float: ...  # [W]

## 5.4 components/pipe.py

| Parameter | Description |
| --- | --- |
| D_i [m] | Inner diameter |
| L [m] | Length |
| roughness [m] | Wall roughness for friction factor |
| orientation | HORIZONTAL / VERTICAL_UP / VERTICAL_DOWN |
| Q_loss [W] | Heat loss to ambient (default 0) |

Pressure drop = ΔP_friction + ΔP_gravity + ΔP_acceleration. Two-phase uses configurable ΔP correlation (default: homogeneous). Single-phase uses Blasius or Churchill.

## 5.5 components/evaporator.py

Microchannel evaporator with zone-based model (subcooled → two-phase → possible superheated). Heated by electronic components at specified heat flux.

| Parameter | Description |
| --- | --- |
| N_ch | Number of parallel microchannels |
| L_ch [m] | Channel length |
| D_h [m] | Hydraulic diameter |
| W_ch, H_ch [m] | Channel width and height (rectangular) |
| Q_evap [W] | Total heat input from electronics |
| htc_correlation | HTC strategy object (default: Shah) |
| dp_correlation | ΔP strategy object (default: MSH) |
| x_out_max | Maximum outlet quality (default 0.8) |

Key outputs: outlet FluidState, pressure drop, average wall temperature, HTC profile along channel, boiling curve (q vs. ΔT_wall).

## 5.6 components/condenser.py

Plate heat exchanger: refrigerant side (hot) condensing against water coolant side (cold). Three-zone model: desuperheating → condensation → subcooling.

- Refrigerant side: Yan correlation for condensation HTC (per Kokate PhD 2024)

- Water side: Dittus-Boelter for single-phase forced convection

- Effectiveness-NTU method for each zone

- Coolant parameters: T_in_water, mdot_water, configurable

## 5.7 components/pump.py

- Characteristic curve: ΔP_pump = f(mdot) — polynomial fit from datasheet or user-defined

- Isentropic efficiency: η_pump = ΔP_ideal·v_l / W_shaft

- NPSH requirement check: P_in > P_sat + ΔP_NPSH

- Outlet state: h_out = h_in + v_l·ΔP_pump / η_pump (isentropic + irreversibility)

## 5.8 components/accumulator.py

The accumulator is the system pressure regulator — its model is critical for both SS and dynamic simulations (Lee 2022, Truster 2024, VanGerner 2016).

- Two types implemented: HCA (Heat Controlled) and PCA (Pressure Controlled)

- SS model: polytropic gas compression P·V^n = const, liquid inventory balance

- Mass conservation: m_total = m_loop + m_accu = const

- Pressure set by accumulator temperature (HCA) or bellows pressure (PCA)

- Dynamic model (Phase 9): ODE for gas volume, liquid level, heat exchange

## 5.9 loop.py — SS Loop Solver

Assembles components in sequence and closes the loop using Newton-Raphson iteration. Solves for the two unknowns that close the loop: system pressure P_sys and mass flow rate mdot.

# Loop closure conditions (residuals driven to zero):

R1 = P_pump_outlet - sum(ΔP_components) - P_pump_inlet  # pressure balance

R2 = h_accumulator_setpoint - h_loop(P_sys)             # pressure regulation

- Input: list of components in order, accumulator setpoint, Q_evap, coolant conditions

- Output: full loop FluidState at each node, operating point (mdot, P_sys, x_out)

- Convergence: Newton-Raphson with Jacobian, tolerance 1e-6

- Parametric sweep: built-in capability for Q_evap vs. T_wall, ΔP vs. mdot maps

## 5.10 dynamic/mbm.py — Moving Boundary Model

The Moving Boundary Method (MBM) tracks the liquid-vapour boundary position within heat exchangers, giving efficient dynamic simulation. Based on Cho (2025) and referenced in Truster (2024).

- Evaporator: two zones (subcooled liquid zone L1, two-phase zone L2 = L_total - L1)

- State variables: L1(t), P(t), h_out(t), mdot(t), T_wall(t)

- Zone boundary moves dynamically as heat load changes — key for capturing start-up and step responses

- Condenser: three zones (vapor, two-phase, liquid) with analogous formulation

- ODE form: dX/dt = f(X, u) — integrated with SciPy BDF (stiff solver)

## 5.11 stability.py — Instability Analysis

| Instability type | Detection method | Reference |
| --- | --- | --- |
| Ledinegg | dΔP_ext/dG < dΔP_int/dG at operating point — negative slope criterion | Kokate PhD 2024 |
| Density Wave Oscillation (DWO) | Linearize ODE system → eigenvalues with positive real part → unstable | Dogan 1983 |
| Pressure Drop Oscillation (PDO) | Compressible volume (accumulator) + negative ΔP characteristic → limit cycle in simulation | Lee 2022 |

Output: stability maps in (G, q'') space; accumulator sizing guidelines; operating envelope for safe loop design.

# 6. Testing & Validation Strategy

## 6.1 Unit testing per module

Each module has its own test file in tests/. Tests follow the pattern: (1) physical consistency checks, (2) analytical limit verification, (3) spot-check against known values.

| Test file | Coverage | Tests | Status |
| --- | --- | --- | --- |
| test_fluid_properties.py | Phase detection, HEM density, void fraction, Cicchitti, all fluids | 67 | Completado |
| test_correlations.py | Shah HTC range check, Kim ΔP monotonicity, single-phase limits | ~40 | Pendiente |
| test_components/test_pipe.py | Hagen-Poiseuille limit, incompressible mass balance, adiabatic | ~25 | Pendiente |
| test_components/test_evaporator.py | Energy balance, outlet quality bounds, wall temperature | ~30 | Pendiente |
| test_loop.py | Mass conservation, loop closure, pump-curve crossing | ~20 | Pendiente |

## 6.2 Validation datasets from literature

| Source | Fluid | Conditions | Validates |
| --- | --- | --- | --- |
| Kokate & Park 2023 | R134a, microchannels | G=100-600, q=1-35 W/cm² | Evaporator SS, Shah HTC |
| Li 2021 | Acetone — primary fluid | Loop-level measurements | Full SS loop, acetone props |
| Wang 2023 | Refrigerant, data center | 1-10 kW loop | Full SS loop, data center |
| Middelhuis 2024 | CO2, parallel evaporators | Multi-evaporator loop | Loop assembler |
| Truster 2024 | R134a, transient step loads | 0-1200 W step | Dynamic MBM, accumulator |
| VanGerner 2016 | CO2, dynamic loop | MacCormack predictions | Dynamic solver accuracy |

# 7. Multi-Chat Development Workflow

The library is developed one module per chat session. At the start of each new chat, share this document plus the relevant completed Python files. Below is the recommended sequence.

| # | Target module | Input to chat | Output |
| --- | --- | --- | --- |
| 1 | fluid_properties.py | This roadmap doc | fluid_properties.py + tests ← DONE |
| 2 | correlations.py | Roadmap + fluid_properties.py | correlations.py + test_correlations.py |
| 3 | base.py + pipe.py | Roadmap + fluid_props + corr | base.py, pipe.py + tests |
| 4 | evaporator.py | Roadmap + all prior modules | evaporator.py + tests |
| 5 | condenser.py | Roadmap + all prior modules | condenser.py + tests |
| 6 | pump.py + accumulator.py | Roadmap + all prior modules | pump.py, accumulator.py + tests |
| 7 | loop.py (SS solver) | Roadmap + all components | loop.py + test_loop.py |
| 8 | SS Validation | Roadmap + complete SS library | validation/ss/ + plots |
| 9 | mbm.py (Moving Boundary) | Roadmap + complete SS library | mbm.py + tests |
| 10 | solver.py (dynamic loop) | Roadmap + SS + mbm.py | solver.py + integration tests |
| 11 | Dynamic validation | Roadmap + full dynamic library | validation/dynamic/ + plots |
| 12 | stability.py | Roadmap + full library | stability.py + stability maps |

## 7.1 Prompt template for new chats

Use this prompt at the start of each development chat session:

I am building a Python MPL (Mechanical Pumped Loop) simulation library for

two-phase thermal management of power electronics. The project knowledge base

contains 25 reference papers on MPL systems, correlations, and instabilities.

Attached: (1) MPL_Roadmap.docx — full project specification

(2) [list of completed .py files]

Today's task: implement [MODULE NAME] as specified in Section 5.X

of the roadmap. Follow the existing code style from fluid_properties.py:

- Dataclasses with type annotations

- Physical basis documented in docstrings with literature references

- Full pytest test suite covering physical consistency checks

- Strategy pattern for interchangeable correlations

# 8. Key Design Decisions & Rationale

| Decision | Choice | Rationale |
| --- | --- | --- |
| State variables | (P, h) — pressure + enthalpy | VanGerner 2016: avoids phase-region discontinuities, natural for HEM |
| Two-phase model | Homogeneous Equilibrium Model (HEM) | Validated for MPL by Kokate 2023, Dogan 1983. Good accuracy for low-x flows. |
| Primary HTC correlation | Shah (1982) for boiling | Lowest MAE (37.2%) in Kokate 2024 comparison for microchannels |
| Primary ΔP correlation | Homogeneous + Kim 2013 | Homogeneous validated by Gholamreza 2016. Kim 2013 for mini/micro accuracy. |
| Dynamic model | Moving Boundary Model (MBM) | Cho 2025: computationally efficient, avoids fine spatial grid, good for control studies |
| ODE solver | SciPy BDF (stiff) or Radau | Two-phase loops are stiff ODEs (fast pressure waves vs. slow thermal transients) |
| Correlation pattern | Strategy Pattern (Protocol classes) | Swap correlations without modifying component code. Enables systematic comparison. |
| Accumulator position | Between condenser and pump (liquid line) | Lee 2022: most stable PDO-free configuration for electronics cooling |

## 8.1 Known limitations & future work

- CoolProp 7.2 lacks viscosity for Acetone and conductivity for R1233ZDE → empirical fallbacks in use (~10-15% accuracy). Upgrade to REFPROP backend if higher accuracy needed.

- HEM assumes equal phase velocities — valid for high-mass-flux, small-diameter channels. For low-quality slug flow, a drift-flux model would be more accurate.

- MBM assumes uniform cross-section and heat flux per zone — not valid for highly non-uniform heating. Extend to finite-volume for localized hot spots.

- Stability analysis linearizes around SS operating point — valid only for small perturbations. Large-amplitude oscillations require full nonlinear simulation.

- Future: parallel evaporator flow maldistribution model (relevant for multi-chip cooling)

- Future: CHF (Critical Heat Flux) prediction using Mudawar's universal correlation

# 9. Nomenclature

| Symbol | Description | Unit | Notes |
| --- | --- | --- | --- |
| P | Pressure | Pa | Primary state var |
| h | Specific enthalpy | J/kg | Primary state var |
| T | Temperature | K |  |
| ρ | Density | kg/m³ | Mixture (HEM) |
| G | Mass flux | kg/m²·s | G = ṁ/A_c |
| ṁ | Mass flow rate | kg/s |  |
| x | Vapour quality | — | 0=sat. liq, 1=sat. vap |
| α | Void fraction | — | Homogeneous model |
| h_fg | Latent heat | J/kg | h_v − h_l |
| μ | Dynamic viscosity | Pa·s |  |
| μ_tp | Two-phase viscosity | Pa·s | Cicchitti model |
| k | Thermal conductivity | W/m·K |  |
| Pr | Prandtl number | — | μ·c_p/k |
| σ | Surface tension | N/m |  |
| D_h | Hydraulic diameter | m | 4A_c/P_wet |
| Re | Reynolds number | — | G·D_h/μ |
| Bo | Boiling number | — | q''/G·h_fg |
| Nu | Nusselt number | — | α·D_h/k |
| α_HTC | Heat transfer coeff. | W/m²·K |  |
| ΔP | Pressure drop | Pa |  |
| Q | Heat transfer rate | W |  |
| q'' | Heat flux | W/m² |  |
| P_red | Reduced pressure | — | P/P_crit |
| η | Efficiency | — | Pump isentropic |

# 10. References

[1] Dogan, T. (1983). Forced-convection boiling flow instabilities. Int. J. Heat Fluid Flow.

[2] Kokate, R. & Park, C. (2023). Pumped two-phase loop — steady-state model. Applied Thermal Engineering.

[3] Kokate, R. (2024). PhD Thesis — P2PL thermal-hydraulic analysis. University.

[4] VanGerner, H. (2016). Dynamic model for MPL. International Conference on Environmental Systems.

[5] Cho, H. (2025). Dynamic Moving Boundary Model for MPL. Journal of Thermal Science.

[6] Kim, S.M. & Mudawar, I. (2012). Universal HTC for two-phase flow. Int. J. Heat Mass Transfer, 55.

[7] Kim, S.M. & Mudawar, I. (2013). Universal flow boiling ΔP. Int. J. Heat Mass Transfer, 56.

[8] Lee, J. et al. (2022). Accumulator effects on MPL instabilities. Int. J. Heat Mass Transfer, 198.

[9] Truster, N. et al. (2024). PCA and MPC control in MPL. Energies, 17, 6347.

[10] Middelhuis, M. et al. (2024). Analysis and validation of pumped two-phase loop. Heat Mass Transfer, 60.

[11] Li, Z. et al. (2021). Experimental investigation MPL with acetone. Applied Thermal Engineering.

[12] Li, Z. et al. (2022). Thermal control of MPL for power electronics. Energies.

[13] Wang, X. et al. (2023). MPL modeling for data center cooling. Applied Energy.

[14] Gerner, H. (2014). Working fluid selection for MPL — Figure of Merit. ICES.

[15] Gholamreza, B.A. et al. (2016). Flow boiling HTC + ΔP in metal-foam tubes I+II. IJHMT.

[16] Zhang, X. et al. (2019). Developments in MPL technology. Applied Thermal Engineering.

[17] Leveque, A. et al. (2024). MPL dynamics. Thermal Science and Engineering Progress.

[18] Furst, B. et al. (2017). MPL architectures survey. ICES.